## Equations (4)
Inputs | Value | Unit
Operating Voltage | 400 | V | Current Carrying Capacity | 226 | A
Ambient Temperature | 65 | C | Number of cables | 5
Total Load | 1600 | A | Partial Load | 320 | A
Max Current | 1600 | A | Ratio | 0.39
Cable Length | 35 | m | Percentage Voltage Drop | 1.092 | %
Cross section mm | 185 | m

## Percentage Voltage Drop
Inverters | Length(m) INV TO Combiner 1 | cable size | Type Cable | I max (A) | Impedance [90 oC] | Voltage Drop(%) | Combiner | Length(m) Combiner To MDB 1 | cable size | Type Cable | I max (A) | Impedance [90 oC] | Voltage Drop(%)
Inverter1 | 194 | 240 | Alum-XLPE-PVC | 200.5 | 0.32 | 2.59 | Combiner Panel 1 | 30 | 4 x 185 | Alum-XLPE-PVC | 1300 | 0.39 | 0.95
Inverter2 | 192 | 240 | Alum-XLPE-PVC | 200.5 | 0.32 | 2.57
Inverter3 | 189 | 240 | Alum-XLPE-PVC | 200.5 | 0.32 | 2.53
Inverter4 | 187 | 240 | Alum-XLPE-PVC | 200.5 | 0.32 | 2.5
Inverter5 | 133 | 150 | Alum-XLPE-PVC | 200.5 | 0.47 | 2.61
| Length(m) INV TO Combiner 2 | cable size |  |  |  | Voltage Drop(%) | Combiner | Length(m) Combiner To MDB 2 | cable size |  |  |  | Voltage Drop(%)
Inverter6 | 131 | 150 | Alum-XLPE-PVC | 200.5 | 0.47 | 2.57 | Combiner Panel 2 | 25 | 5 x 185 | Alum-XLPE-PVC | 1600 | 0.39 | 0.78
Inverter7 | 129 | 150 | Alum-XLPE-PVC | 200.5 | 0.47 | 2.53
Inverter8 | 126 | 150 | Alum-XLPE-PVC | 200.5 | 0.47 | 2.47
Inverter9 | 124 | 150 | Alum-XLPE-PVC | 200.5 | 0.47 | 2.43
Inverter10 | 112 | 120 | Alum-XLPE-PVC | 200.5 | 0.55 | 2.62
Inverter11 | 115 | 120 | Alum-XLPE-PVC | 133.7 | 0.55 | 1.76
| Length(m) INV TO Combiner 3 | cable size |  |  |  | Voltage Drop(%) | Combiner | Length(m) Combiner To MDB 3 | cable size |  |  |  | Voltage Drop(%)
Inverter12 | 152 | 185 | Alum-XLPE-PVC | 200.5 | 0.39 | 2.48 | Combiner Panel 3 | 35 | 5 x 185 | Alum-XLPE-PVC | 1600 | 0.39 | 1.09
Inverter13 | 155 | 185 | Alum-XLPE-PVC | 200.5 | 0.39 | 2.53
Inverter14 | 157 | 185 | Alum-XLPE-PVC | 200.5 | 0.39 | 2.56
Inverter15 | 200 | 240 | Alum-XLPE-PVC | 200.5 | 0.32 | 2.67
Inverter16 | 203 | 240 | Alum-XLPE-PVC | 200.5 | 0.32 | 2.71
Inverter17 | 205 | 240 | Alum-XLPE-PVC | 200.5 | 0.32 | 2.74

## Aluminum MultiCore
Nominal Area of Conductor | Copper Conductor mV/Amp/m | Aluminum Conductor mV/Amp/m
mm² | PVC Rated 90°C | PVC Rated 90°C
1.5 | 22.6 | -
2.5 | 13.8 | -
4 | 8.6 | -
6 | 5.8 | -
10 | 3.5 | -
16 | 2.2 | 3.6
25 | 1.4 | 2.3
35 | 1.1 | 1.7
50 | 0.8 | 1.3
70 | 0.58 | 0.91
95 | 0.44 | 0.68
120 | 0.37 | 0.55
150 | 0.32 | 0.47
185 | 0.27 | 0.39
240 | 0.23 | 0.32
300 | 0.2 | 0.27
400 | 0.18 | 0.23
500 | 0.15 | 0.2