## Final BOM
Model Name | Quantity | Description of the Part | How to Connect It | Relevant Regulations
Huawei SUN2000-150K-MG0 | 11 | 150kW String Inverter (175kVA max), 1100V DC, 800V AC Output. | DC: connect max 2 strings/MPPT using MC4-Evo2. AC: Use Al/Cu lugs (OT/DT) to 800V Busbar. Comms: RS485 Pin 2/4. | SEC Distribution Code 13.8kV (LVRT/HVRT), IEC 62109-1/2, IEC 61727
Huawei SUN2000-100KTL-M2 | 1 | 100kW String Inverter, 1100V DC, 400/480V AC Output. | DC: Standard MC4. AC: Direct connection to LV Panel. Grounding: PE point on chassis. | SASO IEC 62109, SEC Low Voltage Standards
PV Module 615Wp | 3132 | Monocrystalline Bifacial Module, Pmax 615W, Voc ~50V. | Series connection (MC4). Max 18 modules per string to keep Voc < 1100V at min temp (-10C). | IEC 61215 (Design), IEC 61730 (Safety), MOMRAH Wind Load >2400Pa
PV Module 585Wp | 3294 | Monocrystalline Bifacial Module, Pmax 585W. | Series connection (MC4). Check compatibility with 615W mounting structure. | IEC 61215, IEC 61730
DC Cable 6mm | As per Strings | 1x6mm² Solar Cable (H1Z2Z2-K), Double Insulated, XLPE, Tinned Copper. | Crimping: Use calibrated solar crimper. Min bending radius: 4x OD. Max run: ~80m for <1.5% drop. | EN 50618 (Standard), IEC 62930, NEC 690.31
AC Cable (Main Feeder) | Est. 450m | 4x240mm² + 1x120mm² Aluminum/XLPE/PVC (NA2XY). | Termination: Bi-metallic lugs (Al/Cu). Gland: CW industrial gland for armor continuity. | IEC 60502-1 (LV Cables), SEC Distribution Standards
Voltage Transformer (Schneider) | 1 | Schneider Electric 13.8kV/110V VT, Class 0.5, 50VA (Cat: PE04500301*0). | Primary: Connect to 13.8kV Bus via MV Fuse. Secondary: 2.5mm² wire to Metering/Relay terminals. | IEC 61869-3 (Inductive VTs), SEC Metering Code (requires Cl 0.2S for revenue)
Voltage Indicator (Schneider) | 1 | Neon Voltage Indicator VPIS (Cat: 1733002*0). | Plug-in connection to capacitive divider on bushings. Ground reference required. | IEC 62271-206 (VPIS Standards)
Grounding Cable | Est. 1200m | 1x70mm² Bare Copper Conductor. | Exothermic weld (Cadweld) for underground joints. Bolted lug for equipment frames. | IEEE 80 (Substation Earthing), SEC grounding spec (<1 Ohm)